## Sheet1
BOQ for Solar Energy System at IBB Burewala Branch 833 (Hybrid)- 12 KW- Central Region
S.No | Item | Description |  | Qty | Units | Per unit cost (Rs) | Total Amount (Rs) with out GST | GST % | GST Amount | Total Amount with GST
1 | Solar Panels | Capacity | N-Type 610 Watts | 20 | pcs |  | 0 | 10 | 0 | 0
|  | Brand | Canadian / Jinko /Longi
|  | Quality | Tire - 1, A Grade - Bifacial
|  | Warranty | 12 Years Products and Performance Warranty: 25 Years
2 | Inverter Hybrid | Capacity | 06 KW | 2 | Pcs | 0 | 0 | 18 | 0 | 0
|  | Brand | Inverex Nitrox
|  | Type | Hybrid, Duel MMPT Tyrackers,IP-65 /IP 66 standard built in Wi Fi for remote Monitoring
|  | Efficiency | 93-98%
|  | Warranty | 05 Years.
3 | Battery | Type | Lithium ion Battery bank, Ensure proper BMS connections) with frame installation. | 2 | Pcs |  | 0 | 18 | 0 | 0
|  | Brand | Pylontech
|  | Rating | 48/51V -100AMP.
|  | Warranty | 05 Years.
4 | Distribution Board (DB's) | Type | AC / DC Breakers including Phase Failure, Phase distribution and tagging on breaker should be placed, Pure copper lugs will be used for connection/ cable installation in breakers complete in all respects. | 1 | Job |  | 0 | 18 | 0 | 0
|  | Brand | Schneider/ Chint for AC and DC breakers only
|  | Quality | Ac / DC Breakers original and protectable of the equipment's operations
|  | DB Material | Main DB shall be made of 16 SWG steel sheet total enclosed electro static painted, wall mounted, along with indication lights, volte meter (AMP meter only AC DB) complete votage control Device,in all respects and AC /DC DB shall be installed separately.Ac MCB 2 Pole Breaker for Inverter IN PUT 32AMP (Qty- 03Nos) & MCB 2 Pole Breaker for Inverter OUT PUT (Qty-06 Nos),DC Breaker 2 Pole for string 16/ 32 AMP (Qty- 6Nos) according to the load distrbution.
|  | Other Accessory | Change Over CAMSCO/ Schneider - 02numbers)+ Accessories , UPVC Ducts, PVC Pipes tapes etc., complete in all respects PVC Pipes / Dura Ducts Adam Jee / Dura ducts only).
5 | Cables | Type | AC / DC Cables (DC cable only Flexible - Tin Cu XLPO XLPO PHOTVLTAIC 1500V Flex for String / panels to Inverter) | 1 | Job |  | 0 | 18 | 0 | 0
|  | Brand | FAST/ Pakistan Cable
|  | Quality | 100% Pure Copper and full gauge
|  | Size of Cables | 6mm/10mm for AC /16mm for earthing (From Earth Main Hole to Lighting Arrester and Panels 16mm Cable shall be installed) ensure on the load operation according to the site requirements.
6 | Protection with Surge Protect Device (SPD). | Type | AC / DC - Additional breakers /External Fuse (Ac SPD- 2 number & for DC SPD- 04 Numbers) | 1 | Job |  | 0 | 18 | 0 | 0
|  | Brand | Schneider/Chint (KA rating shall be according to the site requirement)
7 | Earthing | Type | High Conductivity Active Green Earth Station using 38 mm dia tin plated copper pipe including 6" dia, up to 20 FT Pit with 4'x4'x20 in NSL / Ground. and Earth enhancement Electrolytic compound with "Coal ,Salt & Sand with 16mm copper rope ".OR deep boring with 4 inches bore pipe up to "water level "with G-I pipe 2"inch Earth station shall be provided with inspection chamber and heavy duty round MS cover, painted with anti rust paint. The earth lead shall be terminated at the copper pipe using proper cad weld jointing method and . | 2 | Job |  | 0 | 18 | 0 | 0
|  | Earth Value | Less than 5 Ohm
|  | Lightning Arrestor | 100% Pure Copper with Insulator
8 | Structure | Type | Mounted - High Beam Structure | 1 | Job |  | 0 | 18 | 0 | 0
|  | Materials | H- Beam Structural (Mughal) C- Chanel and Cross along with Galvanized bolts, washer, Nuts, red oxide, paint works, Top & Base palates, Epoxy and support accessories , Walkind Pathway for Solar Panels cleaning, complete in all respect (Specification is attached Annex- A)
|  | Civil Works | Included
|  | Warranty | 10 Years
9 | Installation & Commissioning | Project | Installation & Commissioning of Solution Installation of PV Panels & Systems complete in all respects included labor charges complete in all respects and single line Diagram (SLD) to be arranged.(Plz note the both the Inverters are to be installed in parallel to support each units in case of failure one of them). | 1 | Job |  | 0 | 16 | 0 | 0
TOTAL AMOUNT OF SYSTEM With GST | [6 empty] | 0 |  |  | 0
(1) Tier-I Panels Bifacial offered rating available will be used in the solution.
(2) DB will include I/P and O/P Breakers and Protections as required.
(3) Cabling has been added in the solution as per the site survey or standard quantity quoted in the solution and no further cost shall be charged to AKBL.
(4) Civil Works will be carried out either by anchoring with the ground or using pre-fab blocks and cost are included in above quoted amount.
(5) No additional cost will be charged from Askari Bank Limited.
(6) Incase of standard structure installation is required the cost will be finalized as per the market price.
(7) Color Coating of all cables shall be installed as per site requirements.
(8) 100% payment will be paid on completion of work.
(9) Quoted price should be valid for 02 Months.
(10) The above quoted amount inclusive GST , GST shall be paid on submission of GST Invoice only.

## Annex A
Annex- A
ELEVATED STRUCTURE MATERIAL SPECIFICATIONS
H-Beam | C-Channel
Brand: Mughal | Brand: Local
Material: MS | Material: Galvanize
Width: 5" | Width: 3"
Depth: 2.5" | Depth: 1.5"
Thickness: 10/11 SWG | Thickness: 14 SWG
Base Plate: | Cross Engle Iron:
Brand: Local | Brand: Local
Material: MS | Material: MS
Width: 8" | Width: 1.5"
Length: 8" | Depth: 1.5"
Thickness: 6mm | Gauge: 16 SWG
STANDARD STRUCTURE MATERIAL SPECIFICATIONS
Channel | L3 SPECS:
Brand: Local | Length: 8'
Material: GI | Base Holders: 4
Width: 3" | L3 SPECS:
Depth: 1.5" | Length: 12'
Thickness: 14 SWG | Base Holders: 6
CIVIL PADS SPECIFICATIONS
Elevated Structure | Pads
Brand: Local | Height:12"
Down Side: 4' | Width: 12"
Hight up to : 8 ' to 10' where suitable degree required at site | Length: 12"
Material: Concrete